## Sheet1
9600 8-bit data, 1 stop bit, no parity
支持modbus协议 3 6 16 数据格式为高位在前,低位在后
Message protocol format: read register, request frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
字段定义 | ADDR | CMD | MSB | LSB | MSB | LSB | CRC-L | CRC-H
描述 | 0xD2 | 0x03 | Register start addr |  | number of registers N |  | CRC-16
Description: D2 03 00 0C 00 01 57 AA D2 is the slave address, 03 is the read command, 000C is the register start address, 0001 means that the number of read registers is 1, that is, the read command, and 57AA is the CRC check code.
Regular response frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
字段定义 | ADDR | CMD | Length | MSB | LSB | MSB | LSB | CRC-L | CRC-H
描述 | 0xD2 | 0x03 | Data length L=2*N | The value of the first register |  | ... the value of the Nth register |  | CRC-16
Description: N is register data D2 03 02 00 01 FC 56 D2 is the slave address, 03 is the read command, 02 is the length of the read data, 0001 means the value of the first register read, that is, the host command is the discharge state, and FC56 is the CRC check code.
Message protocol format: write register, request frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
字段定义 | ADDR | CMD | MSB | LSB | MSB | LSB | CRC-L | CRC-H
描述 | 0xD2 | 0x06 | Register address |  | data |  | CRC-16校验
Description: D2 06 00 0C 00 01 9B AA D2 is the slave address, 06 is the instruction to write a single holding register, 000C is the register address, 0001 is the host commanding battery discharge, and 9BAA is the CRC check code
Regular response frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
字段定义 | ADDR | CMD | MSB | LSB | MSB | LSB | CRC-L | CRC-H
描述 | 0xD2 | 0x06 | Register address |  | data |  | CRC-16校验
Note: The format of the general response frame for writing a single holding register is the same as that of the request frame.
Message protocol format: write multiple data registers, request frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
字段定义 | ADDR | CMD | MSB | LSB | MSB | LSB | MSB | LSB | CRC-L
描述 | 0xD2 | 0x10 | Register start addr |  | Register length(N) |  | Data content(2N) |  | CRC-16校验
Description: D2 10 00 0C 00 02 00 01 00 02 7D 65 0xD2 is the slave address, 0x10 indicates the instruction to write multiple data registers, 0x000C is the register start address, 0x0002 indicates two registers are written consecutively, 0x0001 indicates the data written in the first register, 0x0002 indicates the second register writes Data, 0x7D65 represents CRC16 check code.
Regular response frame
BYTE | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
字段定义 | ADDR | CMD | MSB | LSB | MSB | LSB | CRC-L | CRC-H
描述 | 0xD2 | 0x10 | Register astart addr |  | Register length(N) |  | CRC-16校验
Description: D2 10 00 0C 00 02 92 68 0xD2 is the slave address, 0x10 is the instruction to write multiple data registers, 0x000C is the register start address, 0x0002 means to write two registers in succession, and 0x9268 means the CRC16 check code.

## Sheet2
保护板协议说明
Data format: 9600 8-bit data, 1 stop bit, no parity
支持modbus协议 3 6 16 | The data format is high order first and low order last
地址 | 数据类型 | 读写 | 内容 | 范围 | 数据计算说明
0x00~0x1F | unsigned int | R | Single battery voltage, every two bytes is a battery voltage | 0--5000 | 0.001 3550*0.001=3.550v
0x20~0x27 |  | R | Battery temperature | 0--140（-40至100℃） | The temperature data is offset by 40, for example, when the temperature data is 40, the actual temperature = temperature data -40;
0x28 |  | R | Total battery voltage |  | 0.1V 350*0.1=35.0v
0x29 |  | R | Current data | 0--65535 | 0.1A, 30000 Offset, the charging current is a negative number, the discharge is a positive number, (30080-30000)*0.1=8A, which is the discharge current
0x2A |  | R | SOC | 0--65535 | 0.001,800/1000=80%
0x2B |  | R | Maximum cell voltage | 0--65535 | 1mv
0x2C |  | R | Lowest cell voltage | 0--65535 | 1mv
0x2D |  | R | Maximum monomer temperature | 0--65535 | 1°C, temperature data offset 40, for example, when temperature data is 40, actual temperature = temperature data -40;
0x2E |  | R | Minimum monomer temperature | 0--65535 | 1°C, temperature data offset 40, for example, when temperature data is 40, actual temperature = temperature data -40;
0x2F |  | R | Charge and discharge state | 0--65535 | 0 static, 1 charge, 2 discharge
0x30 |  | R | Battery remaining capacity |  | 0.1AH
0x31 |  | R | Number of batteries
0x32 |  | R | Number of battery temperature sensors
0x33 |  | R | Number of battery cycles
0x34 |  | R | Balancing | 0--65535 | 0: Off 1: On
0x35 |  | R | Charging MOS status | 0--65535 | 0: Off 1: On
0x36 |  | R | Discharge MOS state | 0--65535 | 0: Off 1: On
0x37 |  | R | Average voltage | 0--65535 | 1mV
0x38 |  | R | Differential pressure | 0--65535 | 1mV
0x39 |  | R | power | 0--65535 | W
0x3A |  | R | Fault status 1 | 0--65535 | Byte 0 Bit 0: Unit voltage is too high level one alarm Bit 1: Unit voltage is too high level 2 alarm Bit 2: Unit voltage is too low level one alarm Bit 3: Unit voltage is too low level 2 alarm Bit 4: Total pressure is too high level one alarm Bit 5: Total pressure is too high level 2 alarm Bit 6: Total pressure is too low one level alarm Bit 7: Total pressure is too low level 2 alarm Byte 1 Bit 0: One level alarm when charging temperature is too high Bit 1: High charging temperature secondary alarm Bit 2: The charging temperature is too low one level alarm Bit 3: Low charging temperature secondary alarm Bit 4: High discharge temperature alarm Bit 5: High discharge temperature secondary alarm Bit 6: Discharge temperature is too low one level alarm Bit 7: Low discharge temperature level 2 alarm
0x3B |  | R | Fault status 2 | 0--65535 | Byte 0 Bit 0: Charge overcurrent level 1 alarm Bit 1: Charge overcurrent secondary alarm Bit 2: Discharge overcurrent level 1 alarm Bit 3: Discharge overcurrent secondary alarm Bit 4: SOC high level alarm Bit 5: SOC is too high level 2 alarm Bit 6: SOC low level alarm Bit 7: Low SOC level 2 alarm Byte 1 Bit 0: One level alarm for excessive pressure difference Bit 1: Excessive pressure difference level 2 alarm Bit 2: An alarm of excessive temperature difference Bit 3: Excessive temperature difference secondary alarm Bit 4~Bit7: Reserved
0x3C |  | R | Fault status 3 | 0--65535 | Byte 0 Bit 0: Charging MOS over temperature warning Bit 1: Discharge MOS over temperature warning Bit 2: Charging MOS temperature detection sensor failure Bit 3: Discharge MOS temperature detection sensor failure Bit 4: Charging MOS adhesion failure Bit 5: Discharge MOS adhesion failure Bit 6: Charging MOS open circuit fault Bit 7: Discharge MOS open circuit fault Byte 1 Bit 0: AFE acquisition chip failure Bit 1: Single acquisition is offline Bit 2: Single temperature sensor failure Bit 3: EEPROM storage failure Bit 4: RTC clock failure Bit 5: Pre-charge failed Bit 6: Vehicle communication failure Bit 7: Intranet communication module failure
0x3D |  | R | Fault state 4 | 0--65535 | Byte 0: Bit 0: Current module failure Bit 1: Internal total pressure detection module failure Bit 2: Short circuit protection failure Bit 3: Low voltage prohibit charging fault Bit 4~Bit7: Reserved