## Form
[7 empty] | CZ | Napětové okno |  | Proudové okno
4
| Panel |  | 3
| V serii |  | 2 |  | Paralelně | 5
24
| Celkový výkon PV |  | 2250 | Wp
|  |  |  | 10 |  | 0
| Teplota panelu |  | Min. | -15 | Max. | 70 |  |  | 2.5
[8 empty] | 12 | 4
| Regulátor | 25 | [5 empty] | 24 | 6
[8 empty] | 36 | 10
| Systémové napětí |  |  | 2 | Volt |  |  | 48 | 25
| Délka Kabelu do MPPT * |  |  | 14 | Průřez: | 6 | 3
* Délka jedním směrem
| Max vstup napětí |  |  |  | 200
| Max napětí PV MIN Teplota |  |  |  | 81.3272
| Min vstup napětí @ MPP |  |  |  | 30
| Min napětí PV MAX Teplota |  |  |  | 43.4561
| Max výstup proud |  |  |  | 80 | Actual current
| Max proud@ MPP min. temp. |  |  |  | 80 | 98.8501
* Výkonový limit @ nizká tep.
| Max proud @ MPP max. temp. |  |  |  | 77.3569 | 77.3569
| Konfigurace panelů |  |  |  | Akceptováno | Akceptováno | Neakceptováno
| Max temp. Watt |  |  |  | 2320.7067
| Min temp. Watt |  |  |  | 2965.5027
áno | [6 empty] | Ne | FALSE
Příklad lokací s očekávanou teplotou | [5 empty] | Min. | Max.
Plochá karavan ,celý rok,špatná ventilace | [5 empty] | 0 | 70
Plochá karavan,léto,špatná ventilace | [5 empty] | 15 | 70
Plochá na lodi, dobrá ventilace | [5 empty] | 10 | 65
Zvednutá na lodi | [5 empty] | 5 | 60
Zvednutá na střeše, teplý region | [5 empty] | 5 | 70
Zvednutá na střeše, průměr region | [5 empty] | 0 | 65
Zvednutá na střeše, studený region | [5 empty] | -5 | 60

## Modules
| Manufacturer | Type | Power | Vmpp | Impp | Voc | Isc | V temp coeff | I temp coeff | Dimension
| [name] | [name] | [W] | [V] | [A] | [V] | [A] | [%/°C] | [%/°C]
Sunny Poly 160Wp 36 cells | Sunny Poly 160Wp 36 cells |  | 160 | 19.17 | 8.35 | 22.76 | 8.95 | -0.38 | 0.06
Scheuten Solar 210 Wp P6-54 | Scheuten Solar 210 Wp | P6-54 | 210 | 25 | 6.12 | 31.1 | 6.62 | -0.34 | 0.06
Jinko Solar 225 Wp JKM245p-60 | Jinko Solar 225 Wp | JKM245p-60 | 225 | 29.4 | 7.65 | 36.7 | 8.25 | -0.27 | 0.05
Sunny Poly 270Wp 60 cells 270 VL4 | Sunny Poly 270Wp 60 cells | 270 VL4 | 270 | 31.6 | 8.56 | 38.8 | 9.18 | -0.31 | 0.047
(NOCT) GWL EXS-340M-B 253W | (NOCT) GWL EXS-340M-B | 253W | 275 | 32.2 | 7.85 | 38.6 | 8.83 | -0.25 | 0.03
Einnova ESP280 GWL/Sunny-60 cells | Einnova ESP280 | GWL/Sunny-60 cells | 280 | 31.4 | 8.92 | 38.2 | 9.45 | -0.33 | 0.06
Amerisolar AS-EU-6P30- 285W | Amerisolar | AS-EU-6P30- 285W | 285 | 31.7 | 9 | 38.7 | 9.42 | -0.33 | 0.06
Amerisolar 320Wp AS-6M30 | Amerisolar 320Wp | AS-6M30 | 300 | 32.4 | 9.26 | 39.6 | 9.7 | -0.38 | 0.06
DHM60 300W | DHM60 | 300W | 300 | 32.7 | 9.19 | 39.9 | 9.64 | -0.33 | 0.06
Jinko PERC JKM315M-60-V | Jinko PERC | JKM315M-60-V | 315 | 33.2 | 9.49 | 40.7 | 10.4 | -0.28 | 0.06
IBC 320 ZL-MB BLACK | IBC | 320 ZL-MB BLACK | 320 | 32.61 | 9.83 | 39.89 | 10.35 | -0.38 | 0.07 | 1696x1022x40 | 2783 | 8.6969
WINAICO 325 WST-M6 PERC MONO 325W | WINAICO 325 WST-M6 PERC MONO | 325W | 325 | 33.92 | 9.59 | 40.7 | 10.37 | -0.29 | 0.04 | 1665x999x35
(NOCT)GWL EXS-450MHC-B 363W | (NOCT)GWL EXS-450MHC-B | 363W | 336 | 38.6 | 8.7 | 46.2 | 9.38 | -0.26 | 0.04
(STC) GWLEXS-340M-B 340W | (STC) GWLEXS-340M-B | 340W | 340 | 34.2 | 9.94 | 41.7 | 10.5 | -0.33 | 0.06
GWL/POWER ESX-340M-B | GWL/POWER | ESX-340M-B | 340 | 34.2 | 9.94 | 41.7 | 10.5 | -0.3 | 0.05 | 1665*1002*35
GWL EXS-380MHC-B 380W | GWL EXS-380MHC-B | 380W | 380 | 34.8 | 10.92 | 41.3 | 11.69 | -0.38 | 0.06
(STC)GWL EXS-450MHC-B 450W | (STC)GWL EXS-450MHC-B | 450W | 450 | 41.5 | 10.84 | 49.3 | 11.6 | -0.26 | 0.04
Amerisolar AS-6M144-HC-450W | Amerisolar | AS-6M144-HC-450W | 450 | 41.8 | 10.77 | 50.2 | 11.28 | -0.28 | 0.05
Swiss solar IBEX 132MHC-EiGER | Swiss solar | IBEX 132MHC-EiGER | 500 | 40.62 | 12.31 | 48.83 | 13.2 | -0.34 | 0.045
LEAPTON LP210-M-66-MH | LEAPTON | LP210-M-66-MH | 650 | 37.8 | 17.28 | 45.58 | 18.16 | -0.28 | 0.05 | 2384*1303*35
Coefficient support:
If you have the voltage temperature coefficient in mV/°C, here is how to change it to %/°C
Write the Voc value in Volt: |  | 24.1 | V
Write the coefficient value in mV/°C: |  | -77 | mV/°C
The coefficent value in %/°C is now: |  | -0.3195 | %/°C
If you have the current temperature coefficient in mA/°C, here is how to change it to %/°C
Write the Isc value in Ampere: |  | 8.72 | A
Write the coefficient value in mA/°C: |  | 4.7 | mA/°C
The coefficent value in %/°C is now: |  | 0.053899 | %/°C

## Regulator
| Manufacturer | Type | Power @ 12V | Power @ 24V | Power @ 36V | Power @ 48V | Voc max | Voc min | Vmpp min | System Voltage |  |  |  | Ibat max | Efficiency@12 | Efficiency@24 | Efficiency@36 | Efficiency@48
Victron Energy BlueSolar MPPT 75/15 | Victron Energy | BlueSolar MPPT 75/15 | 200 | 400 | 0 | 0 | 75 | 5 | 1 | 12 | 24 | N.A. | N.A. | 15 | 0.98 | 0.98 | 0 | 0
Victron Energy BlueSolar MPPT 75/50 | Victron Energy | BlueSolar MPPT 75/50 | 700 | 1400 | 0 | 0 | 75 | 5 | 1 | 12 | 24 | N.A. | N.A. | 50 | 0.98 | 0.98 | 0 | 0
Victron Energy BlueSolar MPPT 100/15 | Victron Energy | BlueSolar MPPT 100/15 | 200 | 400 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 15 | 0.98 | 0.98 | 0 | 0
Victron Energy BlueSolar MPPT 100/30 | Victron Energy | BlueSolar MPPT 100/30 | 440 | 880 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 30 | 0.98 | 0.98 | 0 | 0
Victron Energy BlueSolar MPPT 100/50 | Victron Energy | BlueSolar MPPT 100/50 | 700 | 1400 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 50 | 0.98 | 0.98 | 0 | 0
Victron Energy BlueSolar MPPT 150/35 | Victron Energy | BlueSolar MPPT 150/35 | 500 | 1000 | 1500 | 2000 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 35 | 0.98 | 0.98 | 0.98 | 0.98
Victron Energy BlueSolar MPPT 150/70 | Victron Energy | BlueSolar MPPT 150/70 | 1000 | 2000 | 3000 | 4000 | 150 | 7 | 2 | 12 | 24 | 36 | 48 | 70 | 0.95 | 0.965 | 0.97 | 0.975
Victron Energy BlueSolar MPPT 150/85 | Victron Energy | BlueSolar MPPT 150/85 | 1200 | 2400 | 3600 | 4850 | 150 | 7 | 2 | 12 | 24 | 36 | 48 | 85 | 0.95 | 0.965 | 0.97 | 0.975
EPEVER XTRA1206N | EPEVER | XTRA1206N | 130 | 260 | 0 | 0 | 60 | 5 | 1 | 12 | 24 | N.A. | N.A. | 10 | 0.95 | 0.965 | 0 | 0
EPEVER XTRA1210N | EPEVER | XTRA1210N | 130 | 260 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 10 | 0.95 | 0.965 | 0 | 0
EPEVER XTRA2210N | EPEVER | XTRA2210N | 260 | 520 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 20 | 0.95 | 0.965 | 0 | 0
EPEVER XTRA3210N | EPEVER | XTRA3210N | 390 | 780 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 30 | 0.95 | 0.965 | 0 | 0
EPEVER XTRA3215N | EPEVER | XTRA3215N | 390 | 780 | 0 | 0 | 150 | 5 | 1 | 12 | 24 | N.A. | N.A. | 30 | 0.95 | 0.965 | 0 | 0
EPEVER XTRA4210N | EPEVER | XTRA4210N | 520 | 1040 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 40 | 0.95 | 0.965 | 0 | 0
EPEVER XTRA4415N | EPEVER | XTRA4415N | 520 | 1040 | 1560 | 2080 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 40 | 0.95 | 0.95 | 0.97 | 0.975
EPEVER XTRA3415N | EPEVER | XTRA3415N | 390 | 780 | 1170 | 1560 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 30 | 0.95 | 0.95 | 0.97 | 0.975
EPEVER Tracer 5210 AN | EPEVER | Tracer 5210 AN | 625 | 1250 | 0 | 0 | 100 | 5 | 2 | 12 | 24 | N.A. | N.A. | 50 | 0.97 | 0.97 | 0.97 | 0.97
EPEVER Tracer 6210 AN | EPEVER | Tracer 6210 AN | 750 | 1500 | 0 | 0 | 100 | 5 | 2 | 12 | 24 | N.A. | N.A. | 60 | 0.97 | 0.97 | 0.97 | 0.97
EPEVER Tracer 5415 AN | EPEVER | Tracer 5415 AN | 625 | 1250 | 1875 | 2500 | 150 | 5 | 2 | 12 | 24 | 36 | 48 | 50 | 0.97 | 0.97 | 0.97 | 0.97
EPEVER Tracer 6415 AN | EPEVER | Tracer 6415 AN | 750 | 1500 | 2250 | 3000 | 150 | 5 | 2 | 12 | 24 | 36 | 48 | 60 | 0.98 | 0.98 | 0.98 | 0.98
EPEVER Tracer 8415 AN | EPEVER | Tracer 8415 AN | 1000 | 2000 | 3000 | 4000 | 150 | 5 | 2 | 12 | 24 | 36 | 48 | 80 | 0.98 | 0.98 | 0.98 | 0.98
EPEVER Tracer 10415 AN | EPEVER | Tracer 10415 AN | 1250 | 2500 | 3750 | 5000 | 150 | 5 | 2 | 12 | 24 | 36 | 48 | 100 | 0.98 | 0.98 | 0.98 | 0.98
EPEVER Tracer 5420 AN | EPEVER | Tracer 5420 AN | 625 | 1250 | 1875 | 2500 | 200 | 5 | 2 | 12 | 24 | 36 | 48 | 50 | 0.97 | 0.97 | 0.97 | 0.97
EPEVER Tracer 6420 AN | EPEVER | Tracer 6420 AN | 750 | 1500 | 2250 | 3000 | 200 | 5 | 2 | 12 | 24 | 36 | 48 | 60 | 0.97 | 0.95 | 0.97 | 0.975
EPEVER Tracer 8420 AN | EPEVER | Tracer 8420 AN | 1000 | 2000 | 3000 | 4000 | 200 | 5 | 2 | 12 | 24 | 36 | 48 | 80 | 0.97 | 0.95 | 0.97 | 0.975
EPEVER Tracer 10420 AN | EPEVER | Tracer 10420 AN | 1250 | 2500 | 3750 | 5000 | 200 | 5 | 2 | 12 | 24 | 36 | 48 | 100 | 0.97 | 0.95 | 0.97 | 0.975
Axpert King 48V 5000W PF1 60-115V | Axpert | King 48V 5000W PF1 60-115V | 0 | 0 | 0 | 4000 | 145 | 72 | 80 | N.A. | N.A. | N.A. | 48 | 80 | N.A. | N.A. | N.A. | 0.9
Axpert VM III 48V 5000W PF1 120-450V | Axpert | VM III 48V 5000W PF1 120-450V | 0 | 0 | 0 | 5000 | 450 | 72 | 80 | N.A. | N.A. | N.A. | 48 | 100 | N.A. | N.A. | N.A. | 0.93
Axpert KING 48V 5000W 60-115V | Axpert | KING 48V 5000W 60-115V | 0 | 0 | 0 | 3000 | 145 | 72 | 80 | N.A. | N.A. | N.A. | 48 | 60 | N.A. | N.A. | N.A. | 0.93

## Calculation table
DATA:
Location: | -15 | min
| 70 | max
Module info: | 73.4 | Voc @25°C
| 58.8 | Vmpp @25°C
| 41.25 | Isc PV@25°C
| 38.25 | Impp PV @25°C
| 93.7125 | Impp output @25°C
| -0.27 | Temp. Coeff. Voc
| -0.19818 | Temp. Coeff. Voc absolute
| 0.05 | Temp. Coeff. Isc
| 0.020625 | Temp. Coeff. Isc absolute
Regulator info: | 200 | Voc max | 80 | Ibat max
5 | 29 | Voc min | 24 | System voltage | 16
| 30 | Vmpp min | 0.95 | Max. Efficiency
Voltage drop: | 0.0178 | Cupper resistance
| 0.083067 | Factor
RESULTS:
[5 empty] | PMw= BATTERY VOLTAGE |  |  | PMw= BATTERY VOLTAGE
Temperature | Voc max. | Voc START min. | Vmpp RUN min. | String Voc max. | String Vmpp max. | String Vmpp corr.max. | String Voc min. | String Vmpp min. | String Vmpp corr. min.
-15 | 200 | 29 | 30 | 81.3272 | 66.7272 | 60.0819
-10 | 200 | 29 | 30 | 80.3363 | 65.7363 | 59.091
-5 | 200 | 29 | 30 | 79.3454 | 64.7454 | 58.1001
0 | 200 | 29 | 30 | 78.3545 | 63.7545 | 57.1092
55 | 200 | 29 | 30 |  | 52.8546 |  | 67.4546 | 52.8546 | 46.2093
60 | 200 | 29 | 30 |  | 51.8637 |  | 66.4637 | 51.8637 | 45.2184
65 | 200 | 29 | 30 |  | 50.8728 |  | 65.4728 | 50.8728 | 44.3366
70 | 200 | 29 | 30 |  | 49.8819 |  | 64.4819 | 49.8819 | 43.4561
Temperature | Ibat max. | Impp PV max. | System Voltage | Ibat max. @ Impp | Ibat min. @ Impp | String I max.
-15 | 80 | 37.425 | 24 | 80 |  | 98.8501
-10 | 80 | 37.5281 | 24 | 80 |  | 97.6505
-5 | 80 | 37.6313 | 24 | 80 |  | 96.4428
0 | 80 | 37.7344 | 24 | 80 |  | 95.2271
55 | 80 | 38.8687 | 24 |  | 80 | 81.3197
60 | 80 | 38.9719 | 24 |  | 80 | 80.0068
65 | 80 | 39.075 | 24 |  | 78.6859 | 78.6859
70 | 80 | 39.1781 | 24 |  | 77.3569 | 77.3569

## Language
V
Pos. | ENGLISH | Czech | ESPANGOL | DEUTSCH | FRANCAIS
1 | Module: | Panel | Módulo FV: | Modul: | Panneau:
2 | In series: | V serii | Cuantos módulos? En Serie: | In Reihe: | En serie:
3 | Parallel: | Paralelně | En paralelo: | Parallel: | Parallèle:
4 | Total PV power: | Celkový výkon PV | Potencia total FV: | PV Leistung insgesamt: | Puissance PV totale:
5 | Wp | Wp | Wp | Wp | Wc
6 | Module temperature: | Teplota panelu | Temp. módulo FV | Modul Temperatur: | Température Paneau:
7 | Min. | Min. | Min. | Min. | Min.
8 | Max. | Max. | Max. | Max. | Max.
9 | Controller: | Regulátor | Reguladorr: | Regler: | Régulateur:
10 | System voltage: | Systémové napětí | Voltaje del sistema: | System Spannung: | Tension du système:
11 | Max. input voltage | Max vstup napětí | Voltaje max. de entrada | Max. Eingangspannung: | Tension d'entrée max.:
12 | Max. PV voltage @ min. temperature | Max napětí PV MIN Teplota | Voltaje max. FV @ Temperatura min. | Max. PV Spannung @ min. Temp. | PV tension max. @ temp. min.
13 | Min. input voltage @ MPP | Min vstup napětí @ MPP | Voltaje min. de entrada @ PMP | Min. Eingangspannung @ MPP | Tension d'entrée min. @ MPP
14 | Min. PV voltage @ max. temperature | Min napětí PV MAX Teplota | Voltaje min. FV @ Temperatura max. | Min. PV Spannung @ max. Temp. | PV tension min. @ temp. max.
15 | Max. output current | Max výstup proud | Corriente max. de salida | Max. Ausgangstrom | Courant de sortie max.
16 | Max. current @ MPP min. temp. | Max proud@ MPP min. temp. | Corriente max. @ PMP temp. min. | Max. Strom @ MPP min. Temp. | Courant max. @ MPP temp. min.
17 | Max. current @ MPP max. temp. | Max proud @ MPP max. temp. | Corriente max. @ PMP temp. max. | Max. Strom @ MPP max. Temp. | Courant max. @ MPP temp. max.
18 | Solar module configuration | Konfigurace panelů | Configuración del módulo FV | Solar Modul Auslegung | Configuration du panneau
19 | Example locations with expected temperatures: | Příklad lokací s očekávanou teplotou | Ejemplos de lugares con temperaturas previstas: | Beispiel Standort und erwartete Temperatur: | Exemple de localisation de site avec la température attendue:
20 | Flat on mobile home, all year (poor ventilation) | Plochá karavan ,celý rok,špatná ventilace | Plano sobre una autocaravana, durante todo el año (mala ventilación) | Flach auf Wohnmobil, ganze Jahr (schlechte Hinterlüftung) | À plat sur toit de camping-car toute l'année (mauvaise ventilation)
21 | Flat on mobile home, only summer (poor ventilation) | Plochá karavan,léto,špatná ventilace | Plano sobre una autocaravana, sólo en verano (mala ventilación) | Flach auf Wohnmobil, nur Sommer (schlechte Hinterlüftung) | À plat sur camping-car , seulement l'été (mauvaise ventilation)
22 | Flat on boat (poor ventilation) | Plochá na lodi, dobrá ventilace | Plano sobre el techo de un barco (mala ventilación) | Flach auf Boot (schlechte Hinterlüftung) | À plat sur ​​le bateau (mauvaise ventilation)
23 | Pitched on boat (good ventilation) | Zvednutá na lodi | Inclinado sobre el techo de un barco (buena ventilación) | Geneigt auf Boot (gute Hinterlüftung) | Inclinée sur bateau (bonne ventilation)
24 | Pitched roof in warm region (good ventilation) | Zvednutá na střeše, teplý region | Techo inclinado en una región cálida (buena ventilación) | Schrägdach, warme Umgebung (gute Hinterlüftung) | Toit en pente, en région chaude (bonne ventilation)
25 | Pitched roof in average region (good ventilation) | Zvednutá na střeše, průměr region | Techo inclinado en una región templada (buena ventilación) | Schrägdach, mittlere Regio (gute Hinterlüftung) | Toit en pente, région tempérée (bonne ventilation)
26 | Pitched roof on mountain (good ventilation) | Zvednutá na střeše, studený region | Techo inclinado en las montañas (buena ventilación) | Schrägdach, in Bergen (gute Hinterlüftung) | Toit en pente, en montagne (bonne ventilation)
27 | * Power limiting @ low temp. | * Výkonový limit @ nizká tep. | * Reducción de potencia @ Temp. baja | * Leistung Begrenzung @ niedrige Temp. | * Limitation de puissance @ basse temp.
28 | ** Power limiting @ high temp. | ** Výkonový limit @ vysoká tep. | ** Reducción de potencia @ Temp. alta | ** Leistung Begrenzung @ hohe Temp. | ** Limitation de puissance @ haute temp.
29 | Voltage window | Napětové okno | Ventana de voltaje | Spannungsfenster | Fourchette de tension
30 | Current window | Proudové okno | Ventana de corriente | Stromfenster | Fourchette de courant
31 | Cable length, Module to MPPT * | Délka Kabelu do MPPT * | Largo de cable entre modulo y MPPT * | Kabel Länge, Modul zum MPPT * | Longuer cable, Paneaux à MPPT *
32 | Cross-section: | Průřez: | Sección: | Querschnitt: | Section:
33 | * One way length | * Délka jedním směrem | * Longitud de un solo cable | * Einfache Distanz | * La distance simple
34 | Are the solar modules covered with snow many periods a year? | áno | ¿Los módulos están cubiertos con nieve durante muchos períodos del año? | Sind die Solar Module öfters im Jahr bedeckt mit Schnee? | Les panneaux PV sont-ils souvent couverts de neige ?
35 | Yes | Ano | Si | Ja | Oui
36 | No | Ne | No | Nein | Non
37 | Accepted | Akceptováno | Aceptado | Erlaubt | Accepté
38 | NOT accepted | Neakceptováno | NO aceptado | NICHT erlaubt | PAS accepté

## Version
History
1.9 | - Added new solar modules, and now 10 additional modules can be added instead of 3.
1.8 | - Added a small calculation on the 'Modules' TAB to help when temperature coefficiences are not in %/°C or %/°K but in mV/°C or mA/°C
1.7 | - Added new solar modules, voltage drop correction and an option to rise the cell temperature in the example list, when the solar modules do not see snow and therefor temperatures will not be so low.
1.6 | - Inserted 4 new regulators and 2 more custom module.
1.5 | - Inserted 4 languages @ updated not applicable (N.A.) voltages for 75/15, 75/50 & 100/15.
1.4 | - Changed texts and Module temperature window.
1.3 | - Power reduction comment set @ highest temperature.
1.2 | - Reduced output current to maximum output current at low & high temperatures. Now a system will show 'power loss' only wenn the output current exceeds the max. at low & high temperatures.
1.1 | - Inserted BlueSolar MPPT 100/15
- Inserted custom module
1.0 | - First version

## List1
Regulator type | Power @ 12V | Power @ 24V | Power @ 48V | Voc max | Ibat max | Modul | Max napětí PV MIN Teplota
EPsolar PMW VS2024AU | 240 | 480 | 0 | 50 | 20
EPsolar XTRA3210 | 390 | 780 | 0 | 100 | 30 | 285W | 81.3272
Modul type | Power | Vmpp | Impp | Voc | Isc
| [W] | [V] | [A] | [V] | [A]
Amerisolar AS-EU-6P30- 285W | 285 | 31.7 | 9 | 38.7 | 9.42
GWL/POWER HS 150W 36cells | 150 | 18 | 8.93 | 22.38 | 8.94
EPsolar XTRA3210
Power @ 12V | 390 | W
Power @ 24V | 780 | W
Power @ 48V | 0 | W
Voc max | 100 | V
Ibat max | 30 | A
Amerisolar AS-EU-6P30- 285W
Modul | 285 | Wp
Vmpp | 31.7 | V
Impp | 9 | A
Rolls 4000 S105 blok 12V 106Ah
Capacity C20 | 85 | Ah
Recommended charge | 10 | A
Max. PV voltage @ min. temperature | 81.3272 | V
Min. PV voltage @ max. temperature | 43.4561 | V
Max. current @ MPP min. temp. | 80 | A
Max. current @ MPP max. temp. | 77.3569 | A