Modbus RTU Protocol

（版权所有，翻版必究）

Ver 117

- Function code of Modbus RTU protocol

The following table lists only the function codes to which this protocol applies.

| Function code | Function code type | Explain | Remark |
| --- | --- | --- | --- |
| 0x03 | Public function code | Read the register | Contains reads to a single register and multiple registers |
| 0x10 | Public function code | Write the register | Contains writes to a single register and multiple registers |

  - Read register (function code: 0x03)

(1) Request the PDU

| Data structure | Data length | Data range |
| --- | --- | --- |
| Function code | 1 byte | 0x03 |
| Starting register address | 2 byte | 0x0000~0xffff |
| Number of registers | 2 byte | 0x0001~ 0x007d |

(2) Normal response PDU

| Data structure | Data length | Data range |
| --- | --- | --- |
| Function code | 1 byte | 0x03 |
| Byte count | 1 byte | N×2 |
| Register values | N×2 byte |  |

Note: N= number of registers

(3)  Abnormal response PDU

| Data structure | Data length | Data range |
| --- | --- | --- |
| Wrong code | 1 byte | 0x83 |
| Exception code | 1 byte | See "exception code" for details. |

(4) Give a typical example

Request to read out three consecutive register values starting at address 107 (describe PDU only) :

| Request |  | Normal response |  | Exceptional response |  |
| --- | --- | --- | --- | --- | --- |
| Field name | Field value | Field name | Field value | Field name | Field value |
| Function code | 0x03 | Function code | 0x03 | Wrong code | 0x83 |
| Starting address Hi | 0x00 | Byte count | 0x06 | Exception code | 0x04 |
| Starting address Lo | 0x6b | Register [107] Hi | 0x02 |  |  |
| Number of registers Hi | 0x00 | Register [107] Lo | 0x2b |  |  |
| Register number Lo | 0x03 | Register [108] Hi | 0x00 |  |  |
|  |  | Register [108] Lo | 0x00 |  |  |
|  |  | Register [109] Hi | 0x00 |  |  |
|  |  | Register [109] Lo | 0x64 |  |  |

  - Write register (function code: 0x10)

(1) Request the PDU

| Data structure | Data length | Data range |
| --- | --- | --- |
| Function code | 1 byte | 0x10 |
| Starting register address | 2 byte | 0x0000~0xffff |
| Number of registers | 2 byte | 0x0001~0x007b |
| Byte count | 1 byte | N×2 |
| Register values | N×2 byte |  |

Note: N= number of registers

(2) Normal response PDU

| Data structure | Data length | Data range |
| --- | --- | --- |
| Function code | 1 byte | 0x10 |
| Starting register address | 2 byte | 0x0000~0xffff |
| Number of registers | 2 byte | 0x0001~0x007b |

(3) Abnormal response PDU

| Data structure | Data length | Data range |
| --- | --- | --- |
| Wrong code | 1 byte | 0x90 |
| Exception code | 1 byte | See "exception code" for details. |

(4) Give a typical example

Request to write 0x000a and 0x0102 to the two registers starting at address 1 (describing only PDU) :

| Request |  | Normal response |  | Exceptional response |  |
| --- | --- | --- | --- | --- | --- |
| Function code | 0x10 | Function code | 0x10 | Wrong code | 0x90 |
| Starting address Hi | 0x00 | Starting address Hi | 0x00 | Exception code | 0x04 |
| Starting address Lo | 0x01 | Starting address Lo | 0x01 |  |  |
| Number of registers Hi | 0x00 | Number of registers Hi | 0x00 |  |  |
| Register number Lo | 0x02 | Register number Lo | 0x02 |  |  |
| Byte count | 0x04 |  |  |  |  |
| Register value Hi | 0x00 |  |  |  |  |
| Register value Lo | 0x0a |  |  |  |  |
| Register value Hi | 0x01 |  |  |  |  |
| Register value Lo | 0x02 |  |  |  |  |

[remark]	Baud rate: 9600bps RS232 or RS485

[remark]	Reserved words, reserved bytes, reserved bits, and unsupported registers are  all filled with 0x00.

[remark]	this protocol is for Microinverter and string inverter

- Registers

| Addr | Name | R/W | Data range | Unit | Note |
| --- | --- | --- | --- | --- | --- |
| 0 | Device type | R |  |  | 0X0200:String inverter, 0X0400:microinverter(MI) |
| 1 | Modbus address | R | [1,247] |  | Modbus address |
| 2 | Communication protocol version | R | 0'~'9':'A'~'Z' |  |  |
| 3 | SN byte 01 | R | 0'~'9':'A'~'Z' |  | The serial number is ten ASCII characters, |
|  | SN byte 02 |  |  |  | If "AH12345678", |
| 4 | SN byte 03 | R | 0'~'9':'A'~'Z' |  | Byte 01 is 0x41 (A), |
|  | SN byte 04 |  |  |  | The 02nd byte is 0x48 (H), |
| 5 | SN byte 05 | R | 0'~'9':'A'~'Z' |  | …… |
|  | SN byte 06 |  |  |  | The 09th byte is 0x37 (7), |
| 6 | SN byte 07 | R | 0'~'9':'A'~'Z' |  | The tenth byte is 0x38 (8). |
|  | SN byte 08 |  |  |  | MI |
| 7 | SN byte 09 | R | 0'~'9':'A'~'Z' |  |  |
|  | SN byte 10 |  |  |  |  |
| 8 | Rated Power | R | 0x0000 |  | 2: singlephase inverter 3:threephase inverter |
| 9 | Chip Type | R | 0x0000 |  | AT32F403A_DEVICE 1 SXX32F103_DEVICE 2 GD32F103_DEVICE 3 GD32F303_DEVICE 4 |
| 10 | LCD Version 2 |  |  |  |  |
| 11 | Slave MCU Version |  |  |  |  |
| 12 | Control MCU Version2 | R |  |  |  |
| 13 | Firmware version of control board | R |  |  | MI |
| 14 | Firmware version of communication board | R |  |  |  |
| 15 | Safety type | R |  |  | MI |
| 16 | Rated power low word | R |  | 0.1W | MI |
| 17 | Rated power high word | R |  | 0.1W | MI |
| 18 | MPPT number and phases | R | [1,8]/[1,3] |  | MI 0x0503: five mppts and three phase |
| 19 | Rated Grid Voltage | R/W | [03] |  | 0: 127/220V 1: 220/380V |
| 20 | Remote Lock | R/W |  |  | OFF 0x0002 ON 0x0000 |
| 21 | Selfcheck time | R/W | [0,1000] | S | MI |
| 22 | System time byte 01 | R/W | [0,255] | Year | Based on the year 2000 |
|  | System time byte 02 | R/W | [1,12] | Month |  |
| 23 | System time byte 03 | R/W | [1,31] | Day |  |
|  | System time byte 04 | R/W | [0,23] | Hour |  |
| 24 | System time byte 05 | R/W | [0,59] | Minute |  |
|  | System time byte 06 | R/W | [0,59] | Sec |  |
| 25 | Minimum insulation impedance | R/W | [100,20000] | 0.1KΩ |  |
| 26 | Dc voltage upper limit | R/W | [2000,10000] | 0.1V |  |
| 27 | Grid voltage Upper limit | R/W | [800,3000] | 0.1V | MI |
| 28 | Grid voltage Lower limit | R/W | [800,3000] | 0.1V | MI |
| 29 | Grid frequency upper limit | R/W | [4500,6500] | 0.01 Hz | MI |
| 30 | Grid frequency lower limit | R/W | [4500,6500] | 0.01 Hz | MI |
| 31 | Grid current Upper limit | R/W | [10,20000] | 0.1A |  |
| 32 | Starting voltage upper limit | R/W | [7000,9000] | 0.1V |  |
| 33 | Starting voltage lower limit | R/W | [4500,9000] | 0.1V |  |
| 34 | Overfrq_Derate_point | R/W | [4500,6500] | 0.01HZ | MI |
| 35 | Overfrq_De_rate | R/W | [0,100] |  | MI |
| 36 | Internal temperature upper limit | R/W | [500,3000] | 0.1℃ |  |
| 37 | Communication address | R | 0x0000 |  | MI |
| 38 | Communication baud rate | R | 0x0000 |  | MI 0:zigbee 1:plc |
| 39 | Power factor regulation | R/W | [0,2000] | 0.001 | The value after the true value is offset by +1000. For example: 0.852 is 148, 0 is 1000, 0.982 is1982 |
| 40 | Active power regulation | R/W | [0,1200] | 0.1%/1% | If 800, adjust to 80.0% |
| 41 | Reactive power regulation | R/W | [0,2000] | 0.10% | 1=0.1%, 800 = 80.0%, 1000 = 100%, 1001= 0.1, 1800 = 80.0%, 2000 = 100% |
| 42 | Apparent power regulation | R/W | [0,1200] | 0.10% | If 800, adjust to 80.0% |
| 43 | Switch on and off enable | R/W | [0,1] |  | 0: power off 1: power on |
| 44 | Feedin Power | R/W | [0,100] |  | 0~100% |
| 45 | Selfchecking time | R/W | [0,1] |  | 0360 seconds |
| 46 | Island protection enable | R/W | [0,1] |  | MI 0: disable 1: enable |
| 47 | MPPT number | R/W | [0,1] |  | MI 0: disable 1: enable |
| 48 | GFDI enable | R/W | [0,1] |  | MI 0: disable 1: enable |
|  | Meter enable |  |  |  | MI 0: disable 1: enable |
| 49 | RCD enable | R/W | [0,1] |  | 0: disable 1: enable |
| 50 | RISO enable | R/W | [0,1] |  | 0: disable 1: enable |
| 51 | Grid Standard | R/W | [0,20] |  | 1：INMETRO 2：EN50549 3：EN50438 4：IEC61727 5：CUSTOM 6：VDE_AR_N_4105 7：UTE_C15_712_1 8：RD_1699 9：CEI_0_21 10：G98_G99 11：AS4777 12：NB/T 32004 |
| 52 | PV curve enable | R/W | [0,1] |  | 0: disable 1: enable |
|  | Meter CT Times |  | [1,5000] |  |  |
| 53 | Max Solar Power | R/W | [0,65536] |  |  |
|  | Hardware Matching |  | Bitmap |  |  |
| 54 | EEPROM initial enabled | R/W | [0,3] |  | 0: normal operation 1: initialize the control board EEPROM 2: initialize the communication board EEPROM |
| 55 | Factory only | R/W | Bitmap |  |  |
| 56 | Limter function enable | R/W | 0x0000 |  |  |
| 57 | Powerwh Factor | R/W |  | 0.01 | 100 mean 1 111 mean 1.11 |
| 58 | RSD enable | R/W | 0x0001 |  | 0x0001 |
| 59 | Run state | R | [0,5] |  | 0x0000 standby 0x0001 selfcheck 0x0002 Normal 0x0003 Warning 0x0004 Fault |
| 60 | Dayactive powerwh | R | [-32768,32767] | 0.1kwh | MI Signed int |
| 61 | Dayreactive powerwh | R | [-32768,32767] | 0.1kvarh | Signed int |
| 62 | Day Grid Work Time | R | [0,65535] | S |  |
| 63 | Total_Active_powerwh low word | R | [0,0xffffffff] | 0.1kwh |  |
| 64 | Total_Active_powerwh high word | R |  |  |  |
| 65 | Total_Reactive_powerwh low word0 | R | [0,0xffff] | 0.1kvarh |  |
| 66 | Total_Reactive_powerwh high word | R | [0,0xffff] | 0.1kvarh |  |
| 67 | Total Work time low word | R | [0,0xffff] | 0.1h |  |
| 68 | Total Work time high word | R | [0,0xffff] | 0.1h | LCD statistics, DLN high status reversed |
| 69 | Inverter efficiency | R | [0,999] | 0.10% |  |
| 70 | Grid voltage AB | R | [0,9999] | 0.1V |  |
| 71 | Grid voltage BC | R | [0,9999] | 0.1V |  |
| 72 | Grid voltage AC | R | [0,9999] | 0.1V |  |
| 73 | Grid voltage A | R | [0,9999] | 0.1V | MI |
| 74 | Grid voltage B | R | [0,9999] | 0.1V |  |
| 75 | Grid voltage C | R | [0,9999] | 0.1V |  |
| 76 | Grid current A | R | [0,65535] | 0.1A | MI |
| 77 | Grid current B | R | [0,65535] | 0.1A |  |
| 78 | Grid current C | R | [0,65535] | 0.1A |  |
| 79 | Grid frequency | R | [0,9999] | 0.01Hz | MI |
| 80 | Displays low power bytes | R | 0x0000 | 0.1W |  |
| 81 | Displays high power bytes | R | 0x0000 | 0.1W |  |
| 82 | Input_active_ power_low word | R | [0,0xffffffff] | 0.1W |  |
| 83 | Input active power high word | R |  | 0.1W |  |
| 84 | Output apparent power low word | R | [0,0xffff] | 0.1VA |  |
| 85 | Output apparent power high word | R | [0,0xffff] | 0.1VA |  |
| 86 | Output active power low word | R | [0,0xffff] | 0.1W | MI |
| 87 | Output active power high word | R | [0,0xffff] | 0.1W |  |
| 88 | Output reactive power low word | R | [0,0xffff] | 0.1Var |  |
| 89 | Output reactive power high word | R |  |  |  |
| 90 | Radiator temperature | R | [0,3000] | 0.1℃ | MI |
| 91 | IGBT temperature | R | [0,3000] | 0.1℃ | 56.2℃indicated as 438 0℃ indicated as 1000 50.5 ℃indicated as 1505 |
| 92 | Inductance 1 temperature (Void) | R | [0,3000] | 0.1℃ |  |
| 93 | Power factor | R |  | [0,1000] |  |
| 94 | SD Card Status | R | [0,3000] | 0.1℃ | 1000 indicated as SD fault，2000 normal |
| 95 | Environment temperature | R | [0,3000] | 0.1℃ |  |
| 96 | Historypv powerwh low word | R | [0,0xffffffff] | 0.1kwh |  |
| 97 | Historypv powerwh high word | R |  | 0.1kwh |  |
| 98 | RCD leak current | R | [0,65535] | 0.01A |  |
| 99 | Limter power | R | 0x0000 | 1W |  |
| 100 | Other test flag bits | R | Bitmap |  | Bit0 arc communication sign Bit8 liion battery interface RS485 Bit9 Liion battery interface CAN Bit10 buttons 1 2 3 4 |
| 101 | Warning message word 1 | R | [0,65535] |  | See the alarm information coding table |
| 102 | Warning message word 2 | R | [0,65535] |  | See the alarm information coding table |
| 103 | Fault information word 1 | R | [0,65535] |  | See the fault information coding table |
| 104 | Fault information word 2 | R | [0,65535] |  | See the fault information coding table |
| 105 | Fault information word 3 | R | [0,65535] |  | See the fault information coding table |
| 106 | Fault information word 4 | R | [0,65535] |  | See the fault information coding table |
| 107 | Corrected_AH | R | [0,1000] | 1AH | 100 is 100AH |
| 108 | Day PV powerwh | R | [0,65535] | 0.1kwh |  |
| 109 | Dc voltage 1 | R | [0,65535] | 0.1V | MI |
| 110 | Dc current 1 | R | [0,65535] | 0.1A | MI |
| 111 | Dc voltage 2 | R | [0,65535] | 0.1V | MI |
| 112 | Dc current 2 | R | [0,65535] | 0.1A | MI |
| 113 | Dc voltage 3 | R | [0,65535] | 0.1V | MI |
| 114 | Dc current 3 | R | [0,65535] | 0.1A | MI |
| 115 | Dc voltage 4 | R | [0,65535] | 0.1V | MI |
| 116 | Dc current 4 | R | [0,65535] | 0.1A | MI |
| 117 | Alarms Status1 | R | 0x0000 |  |  |
| 118 | Alarms Status2 | R | 0x0000 |  |  |
| 120 | Debug Data |  |  |  |  |
| 121 | Debug Data |  |  |  |  |
| 122 | Debug Data |  |  |  |  |
| 123 | Debug Data |  |  |  |  |
| 124 | Debug Data |  |  |  |  |
| 198 | Input_active_ power_low word | R |  | 1W |  |
| 199 | Input active power high word | R |  | 1W |  |
| 200 | Day_Load_Power Wh |  |  | 0.01kwh |  |
| 201 | History_Load_Power Wh_low word |  |  | 0.1kwh |  |
| 202 | History_Load_Power Wh_high word |  |  | 0.1kwh |  |
| 203 | Meter_active_ power_low word | R |  | 1W | Signed int |
| 204 | Meter active power high word | R |  | 1W | Signed int |
| 205 | Day_ gridsell _Power Wh |  |  | 0.01kwh |  |
| 206 | History_ gridsell _Power Wh_low word |  |  | 0.1kwh |  |
| 207 | History_ gridsell _Power Wh_high word |  |  | 0.1kwh |  |
| 208 | Day_ gridbuy _Power Wh |  |  | 0.01kwh |  |
| 209 | History_ gridbuy _Power Wh_low word |  |  | 0.1kwh |  |
| 210 | History_ gridbuy _Power Wh_high word |  |  | 0.1kwh |  |
| 211 | Dc voltage 5 | R | [0,65535] | 0.1V |  |
| 212 | Dc current 5 | R | [0,65535] | 0.1A |  |
| 213 | Dc voltage 6 | R | [0,65535] | 0.1V |  |
| 214 | Dc current 6 | R | [0,65535] | 0.1A |  |
| 215 | Dc voltage 7 | R | [0,65535] | 0.1V |  |
| 216 | Dc current 7 | R | [0,65535] | 0.1A |  |
| 217 | Dc voltage 8 | R | [0,65535] | 0.1V |  |
| 218 | Dc current 8 | R | [0,65535] | 0.1A |  |
| 227 | Grid Connection Setup Remaining Time | R | [60000,0] | S |  |
| 300 | Grid voltage Upper limit2 | R/W | [800,3000] | 0.1V |  |
| 301 | Grid voltage Upper limit3 | R/W | [800,3000] | 0.1V |  |
| 302 | Grid voltage Lower limit2 | R/W | [800,3000] | 0.1V |  |
| 303 | Grid voltage Lower limit3 | R/W | [800,3000] | 0.1V |  |
| 304 | Grid frequency upper limit2 | R/W | [4500,6500] | 0.01 Hz |  |
| 305 | Grid frequency upper limit3 | R/W | [4500,6500] | 0.01 Hz |  |
| 306 | Grid frequency lower limit2 | R/W | [4500,6500] | 0.01 Hz |  |
| 307 | Grid frequency lower limit3 | R/W | [4500,6500] | 0.01 Hz |  |
| 308 | Grid voltage Upper Tripping time1 | R/W | [5,65000] | 10ms |  |
| 309 | Grid voltage Upper Tripping time2 | R/W | [5, 65000] | 10ms |  |
| 310 | Grid voltage Upper Tripping time3 | R/W | [5, 65000] | 10ms |  |
| 311 | Grid voltage Lower Tripping time1 | R/W | [5, 65000] | 10ms |  |
| 312 | Grid voltage Lower Tripping time2 | R/W | [5, 65000] | 10ms |  |
| 313 | Grid voltage Lower Tripping time3 | R/W | [5, 65000] | 10ms |  |
| 314 | Grid frequency Upper Tripping time1 | R/W | [5, 65000] | 10ms |  |
| 315 | Grid frequency Upper Tripping time2 | R/W | [5, 65000] | 10ms |  |
| 316 | Grid frequency Upper Tripping time3 | R/W | [5, 65000] | 10ms |  |
| 317 | Grid frequency Lower Tripping time1 | R/W | [5, 65000] | 10ms |  |
| 318 | Grid frequency Lower Tripping time2 | R/W | [5, 65000] | 10ms |  |
| 319 | Grid frequency Lower Tripping time3 | R/W | [5, 65000] | 10ms |  |
| 390 | Solar1 do Wind Input can make | R/W | [0,1] |  | 0: disable 1: enable |
| 391 | Solar2 do Wind Input can make | R/W | [0,1] |  | 0: disable 1: enable |
| 392 | Voltage 1 | R/W | [500,5000] | 0.1V |  |
| 393 | Voltage 2 | R/W |  | 0.1V |  |
| 394 | Voltage 3 | R/W |  | 0.1V |  |
| 395 | Voltage 4 | R/W |  | 0.1V |  |
| 396 | Voltage 5 | R/W |  | 0.1V |  |
| 397 | Voltage 6 | R/W |  | 0.1V |  |
| 398 | Voltage 7 | R/W |  | 0.1V |  |
| 399 | Voltage 8 | R/W |  | 0.1V |  |
| 400 | Voltage 9 | R/W |  | 0.1V |  |
| 401 | Voltage 10 | R/W |  | 0.1V |  |
| 402 | Voltage 11 | R/W |  | 0.1V |  |
| 403 | Voltage 12 | R/W |  | 0.1V |  |
| 404 | Current 1 | R/W | [0,200] | 0.1A |  |
| 405 | Current 2 | R/W |  | 0.1A |  |
| 406 | Current 3 | R/W |  | 0.1A |  |
| 407 | Current 4 | R/W |  | 0.1A |  |
| 408 | Current 5 | R/W |  | 0.1A |  |
| 409 | Current 6 | R/W |  | 0.1A |  |
| 410 | Current 7 | R/W |  | 0.1A |  |
| 411 | Current 8 | R/W |  | 0.1A |  |
| 412 | Current 9 | R/W |  | 0.1A |  |
| 413 | Current 10 | R/W |  | 0.1A |  |
| 414 | Current 11 | R/W |  | 0.1A |  |
| 415 | Current 12 | R/W |  | 0.1A |  |