## PV1800 Modbud RTU Protocol 1-4
Register Address(decimal) | Register Type | Register Name | Physical Unit | Effective Range | note | Inverter Control Message
10001 | RO | The type of machine | "PC1600"
10002 | RW | Serial number High
10003 | RW | Serial number Low
10004 | RO | Hardware version | 1.0.00
10005 | RO | Software version | "1.0.00"
10006 | RW | PV voltage calibration coefficient | 16384
10007 | RW | Battery voltage calibration coefficient | 16384
10008 | RW | Charger current calibration coefficient | "16384"
10009 | RW | reserved
10100 | RW | reserved
10103 | RW | Float voltage | 0.1V | 480~584(48.0-58.4)V the default value is 54.0V
10104 | RW | Absorption voltage | 0.1V | 480~584(48.0-58.4)V the default value is 56.4V
10105 | RW | "Battery low voltage(for PV | PH)" | 0.1V | 340~440(34.0-44.0)V the default value is 34.0V
10106 | RW | reserved
10107 | RW | "Battery High voltage(for PV | PH)" | 0.1V | 580~600(58.0-60.0)V the default value is 60.0V
10108 | RW | "PV max charger current(for PV | PH)" | 0.1A | 0.1A effective range:(0-80.0)A
10110 | RW | Battery type | "0:no choose 1:Use defined battery 2:lithium battery3:SEALED_LEAD battery 4:AGM battery 5:GEL battery 6:FLOODED battery " | "the default value is 4 | effective range:0,6"
10111 | RW | Battery AH | 1AH | effective range:(0-900)AH the default value is 100AH
10112 | RW | Remove the accumulated data | 0:No remove the accumulated data 1:Remove the accumulated data | " the default value is 0 | effective range:0,1"
10118 | RW | Battery equalization enable | 0:Disable 1:Enable | "effective range:0,1 the default value is 0 | "
10119 | RW | Battery Equalization voltage | 0.1V | "48V:480-640(48.0-64.0)V the default value is 58.4V 24V:240-320(24.0-32.0)V the default value is 29.2V 12V:120-160(12.0-16.0)V the default value is 14.6V"
10120 | RW | reserved | reserved
10121 | RW | Battery equalized time | 1min | 5-900(5-900)min the default value is 150min
10122 | RW | Battery Equalized timeout | 1min | 5-900(5-900)min the default value is 150min
10123 | RW | Equalization interval | 1day | 0-90(0-90)day the default value is 30 days
10124 | RW | Equalization actived immediately | 0:No effect | 1:Action | " the default value is 0 | effective range:0,1"
15201 | RO | Charger workstate | "0:Initialization mode 1:Selftest Mode 2: Work Mode 3:Stop Mode"
15202 | RO | Mppt state | "0:Stop 1:MPPT 2: Current limiting"
15203 | RO | charging state | "0:Stop 1:Absorb charge 2: Float charge 3:EQ charge"
15204 | RO | reserved
15205 | RO | PV voltage | 0.1V | (0.0-150.0)V
15206 | RO | Battery voltage | 0.1V | (0.0-80.0)V
15207 | RO | Charger current | 0.1A | (0.0-90.0)A
15208 | RO | Charger power | 1W | (0-5000)W
15209 | RO | Radiator temperature | 1? | (-40-150)?
15210 | RO | External temperature | 1? | (-40-150)?
15211 | RO | Battery Relay |  | 0: Disconnect 1:Connect
15212 | RO | PV Relay |  | 0: Disconnect 1:Connect
15213 | RO | Error message | Refer to frame Charger Error message 1
15214 | RO | Warning message | Refer to frame Charger Warning message 1
15215 | RO | BattVol Grade | 1V
15216 | RO | Rated Current | 0.1A
15217 | RO | Accumulated PV power high | 1000KWH
15218 | RO | Accumulated PV power low | 0.1KWH
15219 | RO | Accumulated day | 1day
15220 | RO | Accumulated hour | 1hour
15221 | RO | Accumulated minute | 1minute
Register Address(decimal) | Register Type | Register Name | Physical Unit | Effective Range | note | Inverter Control Message
20000 | RO | The type of machine High | "PH/EP/PV"
20001 | RO | The type of machine Low | 1800/3000
20002 | RW | Serial number High
20003 | RW | Serial number Low
20004 | RO | Hardware version | 1.00.00
20005 | RO | Software version | "1.00.00"
20006 | RO | Communication Protocal Edition | 1.00.00 |  | 1.04.15
20007 | RW | reserved | reserved
20008 | RW | reserved | reserved
20009 | RW | Battery voltage calibration coefficient | 16384
20010 | RW | Inverter voltage calibration coefficient | 16384
20011 | RW | Grid voltage calibration coefficient | "16384"
20012 | RW | Bus voltage calibration coefficient | 16384
20013 | RW | Control Current calibration coefficient | 16384
20014 | RW | Inverter Current calibration coefficient | 16384
20015 | RW | Grid Current calibration coefficient | 16384
20016 | RW | Load Current calibration coefficient | 16384
20101 | RW | Inverter offgrid work enable | 0:OFF 1:ON | "effective range:0,1 the default value is 1 | " | 1:Turn on the inverter output when the grid is off, 0:Shut down the inverter output when the grid is off.
20102 | RW | Inverter output voltage Set | 220.0V-240.0V | (2200-2400) | Set the output voltage amplitude.
20103 | RW | Inverter output frequency Set | 50.00Hz/60.00Hz | 5000/6000 | Set the output frequency.
20104 | RW | Inverter search mode enable | 0:OFF 1:ON | "effective range:0,1 the default value is 0 | " | 0:If disabled, no matter connect load is low or high, the on/off status of inverter output will not be effected, 1:If enable, the inverter begins search mode if the AC load connected is pretty low or not detected. The inverter’s “search” mode reduces stand-by energy consumption during no-load conditions.
20108 | RW | Inverter discharger to grid enable | "48V: 0:OFF 1:ON 24V: Null" | "effective range:0,1 the default value is 1 | " | 1:Enable Inveter discharging from battery to grid when the Inverter is connnectted to Grid 0:Disable Inveter discharging from battery to grid when the Inverter is connnectted to Grid
20109 | RW | Energy use mode | "48V:1:SBU | 2:SUB | 3:UTI | 4:SOL (for PV | PH)1:BAU | 3:UTI | 4:BOU (for EP)12V 24V:1:SBU | 3:UTI | 4:SOL (for PV | PH)1:BU | 3:UTI (for EP)" | refer to user's manual
20111 | RW | Grid protect standard | "0:VDE4105 | 1:UPS | 2:home | 3:GEN" |  | refer to user's manual
20112 | RW | SolarUse Aim | "0:LBU 1:BLU(defalut)(for PV | PH)0:LB 1:LU(defalut) (for EP)"
20113 | RW | Inverter max discharger current | "48V: 0.1A(AC)12V 24V: Null" | 1.0A-21.7A(10-217) | Set the max discharging current from Inverter
20118 | RW | Battery stop discharging voltage | 0.1V | 440~580(44.0-58.0)V the default value is 46.0V | refer to user's manual
20119 | RW | Battery stop charging voltage | 0.1V | 440~580(44.0-58.0)V the default value is 54.0V | refer to user's manual
20125 | RW | Grid max charger current set | 0.1A(DC) | 10~800(1.0-80.0)A the default value is 60.0A
20127 | RW | Battery low voltage | 0.1V | 400~480(40.0-48.0)V the default value is 40.8V
20128 | RW | Battery high voltage | 0.1V | 580~600(58.0-60.0)V the default value is 60.0V
20132 | RW | Max Combine charger current | "0.1A(DC)(for PV | PH)" | 10~1400(1.0-140.0)A the default value is 60.0A
20142 | RW | System setting |  | refer to the frame System setting bit
20143 | RW | Charger source priority | "0:Soalr first (for PV | PH)2:Solar and Utility(default) (for PV | PH)3:Only Solar (for PV | PH)2:Utility charger enable (default) (for EP)3:Utility charger disable (for EP)"
20144 | RW | Solar power balance | "0:SBD 1:SBE"
20213 | RW | Remove the accumulated data | 0:No remove the accumulated data 1:Remove the accumulated data | " the default value is 0 | effective range:0,1"
20214 | RW | Reset the parameter | 0:No effect 1:Action | " the default value is 0 | effective range:0,1"
Register Address(decimal) | Register Type | Register Name | Physical Unit | Effective Range | note | Inverter Display Message
25201 | RO | work state | 0:PowerOn 1:SelfTest 2:OffGrid 3:Grid-Tie 4:ByPass 5:Stop 6:Grid charging
25202 | RO | AC voltage grade | "230:230V 120:120V"
25203 | RO | Rated power(VA) | VA
25204 | RO | reserved
25205 | RO | Battery voltage | 0.1V
25206 | RO | Inverter voltage | 0.1V
25207 | RO | Grid voltage | 0.1V
25208 | RO | BUS voltage | 0.1V
25209 | RO | Control current | 0.1A
25210 | RO | Inverter current | 0.1A
25211 | RO | Grid current | 0.1A
25212 | RO | Load current | 0.1A
25213 | RO | PInverter | 1W
25214 | RO | PGrid | 1W
25215 | RO | PLoad | 1W
25216 | RO | Load percent | 1 % | new
25217 | RO | SInverter | 1VA
25218 | RO | SGrid | 1VA
25219 | RO | Sload | 1VA
25220 | RO | reserved
25221 | RO | Qinverter | 1var
25222 | RO | Qgrid | 1var
25223 | RO | Qload | 1var
25224 | RO | reserved
25225 | RO | Inverter frequency | 0.01Hz
25226 | RO | Grid frequency | 0.01Hz
25227 | RO | reserved
25228 | RO | reserved
25229 | RO | Inverter max number
25230 | RO | Combine type
25231 | RO | Inverter number
25232 | RO | reserved
25233 | RO | AC radiator temperature | 1?
25234 | RO | Transformer temperature | 1?
25235 | RO | DC radiator temperature | 1?
25236 | RO | reserved
25237 | RO | Inverter relay state | 0: Disconnect 1:Connect
25238 | RO | Grid relay state | 0: Disconnect 1:Connect
25239 | RO | Load relay state | 0: Disconnect 1:Connect
25240 | RO | N_Line relay state | 0: Disconnect 1:Connect
25241 | RO | DC relay state | 0: Disconnect 1:Connect
25242 | RO | Earth relay state | 0: Disconnect 1:Connect
25243 | RO | reserved
25244 | RO | reserved
25245 | RO | Accumulated charger power high | 1000KWH
25246 | RO | Accumulated charger power low | 0.1KWH
25247 | RO | Accumulated discharger power high | 1000KWH
25248 | RO | Accumulated discharger power low | 0.1KWH
25249 | RO | Accumulated buy power high | 1000KWH
25250 | RO | Accumulated buy power low | 0.1KWH
25251 | RO | Accumulated sell power high | 1000KWH
25252 | RO | Accumulated sell power low | 0.1KWH
25253 | RO | Accumulated load power high | 1000KWH
25254 | RO | Accumulated load power low | 0.1KWH
25255 | RO | Accumulated self_use power high | 1000KWH
25256 | RO | Accumulated self_use power low | 0.1KWH
25257 | RO | Accumulated PV_sell power high | 1000KWH
25258 | RO | Accumulated PV_sell power low | 0.1KWH
25259 | RO | Accumulated grid_charger power high | 1000KWH
25260 | RO | Accumulated grid_charger power low | 0.1KWH
25261 | RO | Error message 1 |  | Refer to frame Error message 1
25262 | RO | Error message 2 |  | Refer to frame Error message 2
25263 | RO | Error message 3 |  | Refer to frame Error message 3
25264 | RO | reserved
25265 | RO | Warning message 1 |  | Refer to frame Warning message 1
25266 | RO | Warning message 2 |  | Refer to frame Warning message 2
25267 | RO | reserved
25268 | RO | reserved
25269 | RO | Serial number High
25270 | RO | Serial number Low
25271 | RO | Hardware version | 1.00.00
25272 | RO | Software version | 1.00.00
25273 | RO | Batt power | W
25274 | RO | Batt current | A
25275 | RO | Batt voltage grade | "48:48V 24:24V 12:12V"
25276 |  | reserved
25277 | RO | Rated power(W) | W
25278 | RO | Communication Protocal Edition | 1.00.00 |  | 1.04.15
25279 | RO | Arrow Flag | bit |  | Refer to the frame Arrow Flag bit | [9 empty] | System setting bit | Bit | meaning
0 | OverLoadRestartForbid
1 | OverTempRestartForbid
2 | OverLoadBypassForbid
3 | AutoTurnPageFlagForbid
4 | GridBuzzEnable(only use by PV1800)
5 | BuzzForbide(only use by PV1800)
6 | LcdLightEnable
7 | RecordFaultForbid
8 | reserved
9 | reserved
10 | reserved
11 | reserved
12 | reserved
13 | reserved
14 | reserved
15 | reserved
Arrow Flag bit |  |  |  |  | Bit |  | meaning
0 | PVFlag | 0:Inexistence 1:Existence
1 | LoadFlag | 0:Inexistence 1:Existence
2 | BattFlag | 0:Inexistence 1:Existence
3 | GridFlag | 0:Inexistence 1:Existence
4 | PV-to-Machine-Arrow | 0:Disconnect 1:PV-to-Machine
5 | Machine-to-Load-Arrow | 0:Disconnect 1:Machine-to-Load
6 | Machine-Batt-Arrow | "00:Disconnect
7
01:Machine-to-Batt
10:Batt-to-Machine
11:Connect"
8 | Machine-Grid-Arrow | "00:Disconnect
01:Machine-to-Grid
10:Grid-to-Machine
11:Connect"
9
10 | reserved
11 | reserved
12 | reserved
13 | reserved
14 | reserved
15 | reserved