## command
A. | General requirements of the protocol
1. The host computer is the master (Master), and the machine is the slave machine (Slave).
2. After the slave machine receives the data frame from the master, it will respond with a response signal within 50ms. After receiving the response signal, the host computer will send the next frame of data after waiting at least 300ms to ensure reliable data synchronization.
3. It is forbidden to operate at addresses other than the register addresses listed in the table, otherwise it may affect the normal operation of the machine.
4. It is strictly forbidden to continuously issue write operation instructions to the machine, otherwise the service life of the EEPROM chip may be accelerated, and it will eventually become unusable.
B. | Transmission Format
| Baud Rate | 9600bps
| Start bit | 1
| Byte width | 8
| Parity | N
| Stop bits | 1
| Slave address | 1
C. | Packet Format
| Address | Function | Data | CRC checksum
| 8bits | 8bits | N*8bits | 16bits
03h: Function of reading multi registers
06h：Function of writing single register
10h：Function of writing multi registers
D. | Function
1. Function 0x03
| Master（request） |  | Slave（response）
| Address（0x01） |  | address（0x01）
| Function（0x03） |  | function（0x03）
| Data start reg(Hi) |  | Byte count
| Data start reg(Lo) |  | Date 1#-Hi
| Data #of regs(Hi) |  | Date 1#-Lo
| Data #of regs(Lo) |  | ……
| CRC-Lo |  | ……
| CRC-Hi |  | Date n#-Hi
Date n#-Lo
CRC-Lo
CRC-Hi
e.g. Read the “C”parameter （C01-C11）
| request | 01 03 00 00 00 0B 04 0D
| response | 01 03 16 07 D1 07 D1 07 D1 07 D1 00 00 00 34 07 D1 07 D1 07 D1 07 D1 02 51 FC 02
2. Function 0x06
| Master（request） |  | Slave（response）
| address（0x01） |  | address（0x01）
| function（0x06） |  | function（0x06）
| Data start reg(Hi) |  | Data start reg(Hi)
| Data start reg(Lo) |  | Data start reg(Lo)
| Date -Hi |  | Date -Hi
| Date -Lo |  | Date -Lo
| CRC-Lo |  | CRC-Lo
| CRC-Hi |  | CRC-Hi
e.g. 1# Set the heating mode setting temperature to 32℃ （P01）
| request | 01 06 00 1F 00 20 B9 D4
| response | 01 06 00 1F 00 20 B9 D4
e.g. 2# Power on the uint and set it to Energy Conservation Heating Mode
| request | 01 06 00 1E 00 01 28 0C
| response | 01 06 00 1E 00 01 28 0C
3. Function 0x10
| Master（request） |  | Slave（response）
| address（0x01） |  | address（0x01）
| function（0x10） |  | function（0x10）
| Data start reg(Hi) |  | Data start reg(Hi)
| Data start reg(Lo) |  | Data start reg(Lo)
| Data #of regs(Hi) |  | Data #of regs(Hi)
| Data #of regs(Lo) |  | Data #of regs(Lo)
| Byte count |  | CRC-Lo
| Date 1#-Hi |  | CRC-Hi
Date 1#-Lo
……
……
Date n#-Hi
Date n#-Lo
CRC-Lo
CRC-Hi

## content
Reg.address
code | content |  | Hex | Dec | mode | unit | range | remark
Press the key" "to enter the "C " parameter
C01 | Outdoor ambient temperature |  | 0000 | 0 | R | ℃ | /10
C02 | Outside coil temperature |  | 0001 | 1 | R | ℃ | /10
C03 | Exhaust temperature |  | 0002 | 2 | R | ℃ | /10
C04 | Return air temperature |  | 0003 | 3 | R | ℃ | /10
C05 | Reserve |  | 0004 | 4 | R
C06 | Reserve |  | 0005 | 5 | R
C07 | Inside coil temp (after throttle) |  | 0006 | 6 | R | ℃ | /10
C08 | Water inlet temperature |  | 0007 | 7 | R | ℃ | /10
C09 | Water outlet temperature |  | 0008 | 8 | R | ℃ | /10
C10 | Economizer inlet temperature |  | 0009 | 9 | R | ℃ | /10
C11 | Economizer outlet temperature |  | 000A | 10 | R | ℃ | /10
C12 | Reserve |  | 000B | 11 | R
C13 | Sensor failure |  | 000C | 12 | R |  |  | Please refer to the third table (code)for details
C14 | System failure |  | 000D | 13 | R
C15 | Driver failure |  | 000E | 14 | R
C16 | Output status |  | 000F | 15 | R
C17 | Working status |  | 0010 | 16 | R
C18 | AC voltage |  | 0011 | 17 | R | V
C19 | DC voltage |  | 0012 | 18 | R | V
C20 | Actual frequency |  | 0013 | 19 | R | Hz
C21 | EEV open degree |  | 0014 | 20 | R | P
C22 | EVIl-EEV open degree |  | 0015 | 21 | R | P
C23 | Heat pump current |  | 0016 | 22 | R | A | /10
C24 | Compressor current |  | 0017 | 23 | R | A | /10
C25 | DC FAN Speed #1 |  | 0018 | 24 | R | rpm
C26 | Compressor target frequency |  | 0019 | 25 | R | Hz
C27 | DC FAN Speed #2 |  | 001A | 26 | R | rpm
C28 |  |  | 001B | 27 | R
C29 |  |  | 001C | 28 | R
C30 |  |  | 001D | 29 | R
/ | Operating mode |  | 001E | 30 | R/W |  |  | 0:OFF 1: ECO Heating 2: Boost Heating 4：Cooling e.g. if set to 2,the unit will be turned on in Boost heating.
P01 | Target temperature setting in Heating Mode |  | 001F | 31 | R/W | ℃
P02 | Target temperature setting in Cooling mode |  | 0020 | 32 | R/W | ℃
P03 | Reserve |  | 0021 | 33 | R/W | ℃
P04 | Adjustment of temperature difference before restart |  | 0022 | 34 | R/W | ℃ |  | The minimum change in inlet water temperature required for the machine to restart when turned on
P05 | Heat pump ON/OFF when temperature reached 1=ON;0=OFF |  | 0023 | 35 | R/W | / |  | When P05=0, the machine stops when the inlet water temperature reaches the set target temperature, and there is no frequency reduction logic. When P05=1, when the inlet water temperature approaches the target temperature, it enters a down frequency operation and maintains a constant temperature operation.
P06 | Reserve |  | 0024 | 36 | R/W
P07 | Ambient temperature of auxiliary electric heater startup |  | 0025 | 37 | R/W | ℃ |  | When the ambient temperature is below the set value, activate the electric auxiliary heating function (parameter S28=1 is valid)
P08 | Reserve |  | 0026 | 38 | R/W
P09 | Adjustment of P01 maximum value |  | 0027 | 39 | R/W | ℃ |  | Set the maximum set temperature value for limiting the heating mode.
P10 | Reserve |  | 0028 | 40 | R/W
S01 | Reserve |  | 0029 |  | R/W |  | 0/1
S02 | Mode optional |  | 002A |  | R/W |  | 0-6 | 0:Cooling-only 1:heating & cooling 2:Heating-only e.g. if set to 2,the unit only has "heating mode" only.
S03 | Correction value of inlet temperature |  | 002B |  | R/W | ℃ |  | Compensation value for inlet water temperature. The adjustment range is S03/10
S04 | Correction value of outlettemperature |  | 002C |  | R/W | ℃ | -5~15 | Compensation value for outlet water temperature. The adjustment range is S04/10
S05 | The coil temperture for entering defrosting |  | 002D |  | R/W | ℃ | -30~0 | Only when the coil temperature is lower than the set value, the machine can be allowed to enter defrosting.
S06 | The coil temperture for exiting defrosting |  | 002E |  | R/W | ℃ | 2~30 | During defrosting operation, when the coil temperature is higher than the set value, defrosting will be exited.
S07 | Defrosting interval time |  | 002F |  | R/W | min | 25~200 | The minimum interval time for defrosting operation.
S08 | Maximum running time of defrosting |  | 0030 |  | R/W | min | 2~20 | One of the conditions for exiting defrosting operation. When the defrosting operation time exceeds the set value, the machine forcibly exits defrosting.
S09 | Difference between ambient and coil temperature for entering defrosting |  | 0031 |  | R/W | ℃ | 0~10 | One of the conditions for allowing defrosting. Defrosting can only be entered when the difference between the ambient temperature and the coil exceeds the set value.
S10 | Running type of water pump |  | 0032 |  | R/W | / | 0/1/2 | Operation mode of water pump: When S10=0, the water pump remains running after startup. When S10=1, when the temperature reaches the set temperature, the water pump stops running, and then starts running every 30 minutes for 2 minutes to check whether the water temperature meets the starting conditions. When S10=2, when the temperature reaches the set temperature, the water pump will shut down with a delay of 30 seconds until the water temperature meets the starting conditions.
S11 | Initial opening degree of EVI-EXV |  | 0033 |  | R/W | P | 0~520 | When enabling the EVI-EEX adjustment function, the initial opening of the EVI-EEX
S12 | Manually or automatically adjust the compressor frequency |  | 0034 |  | R/W |  | 0/1 | When S12=1, the compressor operates at the set value of S13. When S12=0, the compressor frequency is automatically adjusted according to the operating conditions.
S13 | Frequency of compressor in manual mode |  | 0035 |  | R/W | Hz | 30-120 | When S12=1, the compressor frequency operates according to the set value.
S14 | Ambient temperature of EVI begins running |  | 0036 |  | R/W | ℃ | 0~30 | Allow the environment temperature of EVIl EX to be turned on, and only when it is below the set value can EVIl EX regulation be turned on.
S15 | Manually or automatically adjust the main-EXV openning degree |  | 0037 |  | R/W |  | 0/1 | When S15=1, the opening of Main-EXV remains at the set value of S16. When S15=0, the opening of Main-EXV is automatically adjusted according to the operating conditions.
S16 | Main-EXV openning degree in manual mode |  | 0038 |  | R/W | P | 0~520 | When S15=1, the opening setting value of Main-EXV
S17 | Manually or automatically adjust the EVI-EXV openning degree |  | 0039 |  | R/W |  | 0/1 | When S17=1, the opening of EVI-EXV remains at the set value of S18. When S17=0, the opening of EVI-EXV is automatically adjusted according to operating conditions.
S18 | EVI-EXV openning degree in manual mode |  | 003A |  | R/W | P | 0~520 | When S17=1, the opening setting value of EVI-EXV
S19 | reserve |  | 003B |  | R/W |  | 0-20
S20 | EVI optional |  | 003C |  | R/W |  | 0/1 | EVI function optional. When S20=1, the EVI function of the machine is valid and starts running when the startup conditions are met. When S20=0, the machine's EVI function is invalid.
S21 | EXV Adjustment interval time |  | 003D |  | R/W | s | 10~240 | EXV Adjustment interval time
S22 | Linkage switch(Remoted swtich) optional |  | 003E |  | R/W |  | 0/1 | 0:No /1:Yes
S23 | Main-EXV openning degree of defrosting |  | 003F |  | R/W | P | 0~520 | Main-EXV openning degree of defrosting
S24 | Exhaust temperature of aux-EXV begins running |  | 0040 |  | R/W | ℃ | 0~120 | Exhaust temperature of aux-EXV begins running
S25 | The coil of temperature for entering defrosting(ambient >4℃） |  | 0041 |  | R/W | ℃ | -30~20 | The coil of temperature for entering defrosting(ambient >4℃）
S26 | The coil of temperature for entering defrosting(ambient ≤4℃） |  | 0042 |  | R/W | ℃ | -30~20 | The coil of temperature for entering defrosting(ambient ≤4℃）
S27 | Type of fan |  | 0043 |  | R/W | / | 0/1 | 0：2 AC fans 1：2 DC fans on drive board 2：1 AC fan 3：2 DC fans out of drive board（With a separate fan drive board） 4：N/A 5：1 DC fan on drive board (FAN2 useless) 6：1 DC fan out of drive board（With a separate fan drive board）
S28 | AUX electric heater optional |  | 0044 |  | R/W |  | 0/1 | Optional electric heating function. When S28=0, the electric auxiliary heating function is invalid. When S28=1, the electric auxiliary heating function is effective, and the electric auxiliary heating is started after meeting the conditions.
S29 | Chassis electric heater optional |  | 0045 |  | R/W | / | 0/1 | Optional chassis heating function. When S29=0, the function is invalid. When S29=1, the function is effective, and the chassis heating is started after meeting the conditions.
S30 | Protection value of temperature difference between inlet and outlet water |  | 0046 |  | R/W | ℃ | 5~20 | When the difference between the outlet temperature and the inlet temperature exceeds the set value, the unit will enter protection.
F01 | The maximum frequency of the compressor in cooling mode in different ambient temperature ranges | Ta＞44℃ | 0047 |  | R/W | Hz | 0~120 | 41≤Ta
F02 |  | 44≥Ta＞36℃ | 0048 |  | R/W | Hz | 0~120 | 36≤Ta＜40
F03 |  | 36≥Ta＞28℃ | 0049 |  | R/W | Hz | 0~120 | 31≤Ta＜35
F04 |  | 28≥Ta＞22℃ | 004A |  | R/W | Hz | 0~120 | 23≤Ta＜30
F05 |  | 22≥Ta℃ | 004B |  | R/W | Hz | 0~120 | Ta≤22
F06 | The maximum frequency of the compressor in ECO heating mode in different ambient temperature ranges | Ta≤-11℃ | 004C |  | R/W | Hz | 0~120 | ≤-21
F07 |  | -11＜Ta≤-5℃ | 004D |  | R/W | Hz | 0~120 | -20≤Ta＜-16
F08 |  | -4＜Ta≤3℃ | 004E |  | R/W | Hz | 0~120 | -15≤Ta＜-11
F09 |  | 4＜Ta≤8℃ | 004F |  | R/W | Hz | 0~120 | -10≤Ta＜-6
F10 |  | 9＜Ta≤21℃ | 0050 |  | R/W | Hz | 0~120 | -5≤Ta＜4
F11 |  | 22＜Ta≤27℃ | 0051 |  | R/W | Hz | 0~120 | 5≤Ta＜10
F12 |  | 28＜Ta≤35℃ | 0052 |  | R/W | Hz | 0~120 | 11≤Ta＜19
F13 | The maximum frequency of the compressor in BOOST heating mode in different ambient temperature ranges | Ta≤-11℃ | 0053 |  | R/W | Hz | 0~120 | ≤-21
F14 |  | -10＜Ta≤-5℃ | 0054 |  | R/W | Hz | 0~120 | -20≤Ta＜-16
F15 |  | -4＜Ta≤3℃ | 0055 |  | R/W | Hz | 0~120 | -15≤Ta＜-11
F16 |  | 4＜Ta≤8℃ | 0056 |  | R/W | Hz | 0~120 | -10≤Ta＜-6
F17 |  | 9＜Ta≤21℃ | 0057 |  | R/W | Hz | 0~120 | -5≤Ta＜4
F18 |  | 22＜Ta≤27℃ | 0058 |  | R/W | Hz | 0~120 | 5≤Ta＜10
F19 |  | 28＜Ta≤35℃ | 0059 |  | R/W | Hz | 0~120 | 11≤Ta＜19
F20 | In different ambient temperature ranges, the initial value of the opening degree of the EXV in the cooling mode | Ta≤22℃ | 005A |  | R/W | P | 0~520 | Ta≤25
F21 |  | 22＜Ta≤28℃ | 005B |  | R/W | P | 0~520 | 25≤Ta＜30
F22 |  | 28＜Ta≤36℃ | 005C |  | R/W | P | 0~520 | 30≤Ta＜35
F23 |  | 36＜Ta≤44℃ | 005D |  | R/W | P | 0~520 | 35≤Ta＜40
F24 |  | Ta＞44℃ | 005E |  | R/W | P | 0~520 | 40≤Ta
F25 | In different ambient temperature ranges, the initial value of the opening degree of the EXV in the ECO heating mode | Ta≤-10℃ | 005F |  | R/W | P | 0~520 | ≤-15
F26 |  | -10＜Ta≤-3℃ | 0060 |  | R/W | P | 0~520 | -15＜Ta≤-10
F27 |  | -3＜Ta≤4℃ | 0061 |  | R/W | P | 0~520 | -15＜Ta≤-10
F28 |  | 4＜Ta≤13℃ | 0062 |  | R/W | P | 0~520 | -10＜Ta≤-5
F29 |  | 13＜Ta≤22℃ | 0063 |  | R/W | P | 0~520 | -5＜Ta≤5
F30 |  | 22＜Ta≤28℃ | 0064 |  | R/W | P | 0~520 | 5≤Ta＜13
F31 |  | 28＜Ta≤36℃ | 0065 |  | R/W | P | 0~520 | 13≤Ta＜20
F32 | In different ambient temperature ranges, the initial value of the opening degree of the EXV in the BOOST heating mode | Ta≤-10℃ | 0066 |  | R/W | P | 0~520 | ≤-15
F33 |  | -10＜Ta≤-3℃ | 0067 |  | R/W | P | 0~520 | -15＜Ta≤-10
F34 |  | -3＜Ta≤4℃ | 0068 |  | R/W | P | 0~520 | -10＜Ta≤-5
F35 |  | 4＜Ta≤13℃ | 0069 |  | R/W | P | 0~520 | -5＜Ta≤-1
F36 |  | 13＜Ta≤22℃ | 006A |  | R/W | P | 0~520 | -1＜Ta≤5
F37 |  | 22＜Ta≤28℃ | 006B |  | R/W | P | 0~520 | 5≤Ta＜13
F38 |  | 28＜Ta≤36℃ | 006C |  | R/W | P | 0~520 | 13≤Ta＜20
F39 | In different ambient temperature ranges, the initial value of the opening degree of the EVI-EXV in the heating mode | Ta≤-17℃ | 006D |  | R/W | P | 0~520 | Ta≤-17℃
F40 |  | 5＜Ta≤11℃ | 006E |  | R/W | P | 0~520 | 5＜Ta≤11℃
F41 |  | 4＜Ta≤-7℃ | 006F |  | R/W | P | 0~520 | 4＜Ta≤-7℃
F42 |  | -8＜Ta≤-16℃ | 0070 |  | R/W | P | 0~520 | -8＜Ta≤-16℃
F43 | The opening value of EXV in the oil return state of the compressor |  | 0071 |  | R/W | P | 0~520
F44 | DC fan speed setting value | 1# | 0072 |  | R/W | rpm | 0~1300
F45 |  | 2# | 0073 |  | R/W | rpm | 0~1300
F46 |  | 3# | 0074 |  | R/W | rpm | 0~1300
F47 |  | 4# | 0075 |  | R/W | rpm | 0~1300
F48 |  | 5# | 0076 |  | R/W | rpm | 0~1300
F49 |  | 6# | 0077 |  | R/W | rpm | 0~1300
F50 | The setting value of the exhaust temperature for the forced opening of the EXV |  | 0078 |  | R/W | ℃ | 20~110 | The setting value of the exhaust temperature for the forced opening of the EXV
F51 | The frequency value at which the compressor is prohibited from running (pipe resonance frequency) | 1# | 0079 |  | R/W | Hz | 0~120 | Set the resonance point of the pipeline to avoid the compressor running at this frequency
F52 |  | 2# | 007A |  | R/W | Hz | 0~120
F53 |  | 3# | 007B |  | R/W | Hz | 0~120
F54 |  | 4# | 007C |  | R/W | Hz | 0~120
F55 |  | 5# | 007D |  | R/W | Hz | 0~120
F56 | Deviation value of pipeline resonance frequency point | 1# | 007E |  | R/W | Hz | 0~120 | Resonance point frequency range value.(F51±F56,F52±F57,F53±F58,F54±F59)
F57 |  | 2# | 007F |  | R/W | Hz | 0~120
F58 |  | 3# | 0080 |  | R/W | Hz | 0~120
F59 |  | 4# | 0081 |  | R/W | Hz | 0~120
F60 | reserve |  | 0082 |  | R/W |  |  | (Please do not modify)
F61 | Deviation value of pipeline resonance frequency point | 5# | 0083 |  | R/W | Hz | 0~120 | Resonance point frequency range value.(F61±F59)
F62 | Compressor frequency in defrost running |  | 0084 |  | R/W | Hz | 20~110 | When defrosting,the running frequency of compressor
F63 | Manual defrost |  | 0085 |  | R/W |  | 0/1 | Execute defrost when set to 1(the coil temperture less than S06)
F64 | reserve |  | 0086 |  | R/W |  | 0/1
F65 | In different ambient temperature ranges, the set value of the superheat degree of the EXV in the cooling mode | Ta<15℃ | 0087 |  | R/W | ℃ | -10~20 | Ta≤15
F66 |  | 15℃≤Ta<25℃ | 0088 |  | R/W | ℃ | -10~20 | 15≤Ta＜25
F67 |  | 25℃≤Ta<35℃ | 0089 |  | R/W | ℃ | -10~20 | 25≤Ta＜35
F68 |  | 35℃≤Ta | 008A |  | R/W | ℃ | -10~20 | 35≤Ta
F69 | In different ambient temperature ranges, the set value of the superheat degree of the EXV in the heating mode | Ta<0℃ | 008B |  | R/W | ℃ | -10~20 | Ta≤0
F70 |  | 0℃≤Ta<10℃ | 008C |  | R/W | ℃ | -10~20 | 0≤Ta＜10
F71 |  | 10℃≤Ta＜20℃ | 008D |  | R/W | ℃ | -10~20 | 10≤Ta＜20
F72 | In different ambient temperature ranges, the set value of the superheat degree of the EVI-EXV in the heating mode | Ta<-10℃ | 008E |  | R/W | ℃ | -10~20 | Ta≤-10
F73 |  | -10℃≤Ta | 008F |  | R/W | ℃ | -10~20 | -10≤Ta
F74 | mailing address |  | 0090 |  | R/W |  | 1-254 | Set the address of modbus communication(Please do not modify)
F75 | In different ambient temperature ranges, the set value of the superheat degree of the EXV in the heating mode | 20℃≤Ta<30℃ | 0091 |  | R/W | ℃ | -10~20 | 20≤Ta＜30
F76 |  | 30℃≤Ta | 0092 |  | R/W | ℃ | -10~20 | 30≤Ta
F77 | EVIl-EXV Adjustment interval time |  | 0093 |  | R/W |  | 0~520
F78 | In different ambient temperature ranges, the initial value of the opening degree of the EXV in the ECO heating mode | 36＜Ta≤43℃ | 0094 |  | R/W | P | 0~520 | 20≤Ta＜24
F79 |  | Ta>44℃ | 0095 |  | R/W | P | 0~520 | 25≤Ta
F80 | In different ambient temperature ranges, the initial value of the opening degree of the EXV in the BOOST heating mode | 36＜Ta≤43℃ | 0096 |  | R/W | P | 0~520 | 20≤Ta＜24
F81 |  | Ta>44℃ | 0097 |  | R/W | P | 0~520 | 25≤Ta
F82 | The maximum frequency of the compressor in ECO heating mode in different ambient temperature ranges | 36<Ta<=43℃ | 0098 |  | R/W | Hz | 20~110 | 20≤Ta＜25
F83 |  | Ta>44℃ | 0099 |  | R/W | Hz | 20~110 | 25≤Ta
F84 | The maximum frequency of the compressor in BOOST heating mode in different ambient temperature ranges | 36<Ta<=43℃ | 009A |  | R/W | Hz | 20~110 | 20≤Ta＜25
F85 |  | Ta>44℃ | 009B |  | R/W | Hz | 20~110 | 25≤Ta
F86 | Four-way valve operation mode selection |  | 009C |  | R/W | / | 0/1 | 0：Four-way valve is ON in cooling mode 1: Four-way valve is ON in heating mode (It has been determined according to the pipeline design, please do not modify)
The following parameters cannot be queried on the wire-controller.
| Auto mode optional |  | 00CB |  |  | / |  | Only for swimming pool HP
| Reserve |  | 00CC |  |  | /
| Reserve |  | 00CD |  |  | /
| Reserve |  | 00CE |  |  | /
| Reserve |  | 00CF |  |  | /
| Reserve |  | 00D0 |  |  | /
| Reserve |  | 00D1 |  |  | /
| Reserve |  | 00D2 |  |  | /
| Reserve |  | 00D3 |  |  | /
| Reserve |  | 00D4 |  |  | /
| Reserve |  | 00D5 |  |  | /
| Reserve |  | 00D6 |  |  | /
| Reserve |  | 00D7 |  |  | /
| Reserve |  | 00D8 |  |  | /
| Reserve |  | 00D9 |  |  | /
| Reserve |  | 00DA |  |  | /
| Reserve |  | 00DB |  |  | /
| Reserve |  | 00DC |  |  | /
| Historical fault record 1# (latest) |  | 00DD |  |  | /
| Historical fault record 2# |  | 00DE |  |  | /
| Historical fault record 3# |  | 00DF |  |  | /
| Historical fault record 4# |  | 00E0 |  |  | /
| Historical fault record 5# |  | 00E1 |  |  | /
| RS485 port function |  | 00E2 |  |  | / |  | 0-for other funtion. 1-for modbus function
| Defrosting interval time |  | 00E3 |  |  | s |  | Using when ambient temp <-1℃
| Power supply type of driverboard |  | 00E4 |  |  | / |  | 0: 1-phase mode, 1: 3-phase mode
| Reserve |  | 00E5 |  |  | /
| Reserve |  | 00E6 |  |  | /
| Reserve |  | 00E7 |  |  | /
| Reserve |  | 00E8 |  |  | /
| Reserve |  | 00E9 |  |  | /
| Reserve |  | 00EA |  |  | /
| Reserve |  | 00EB |  |  | /
| Reserve |  | 00EC |  |  | /
| Reserve |  | 00ED |  |  | /
| Reserve |  | 00EE |  |  | /
| Reserve |  | 00EF |  |  | /
| Reserve |  | 00F0 |  |  | /
| Reserve |  | 00F1 |  |  | /
| Reserve |  | 00F2 |  |  | /
| Reserve |  | 00F3 |  |  | /
| 1# water temperature for decreasing target frequency(Boost mode) |  | 00F4 |  |  | ℃
| 2# water temperature for decreasing target frequency(Boost mode) |  | 00F5 |  |  | ℃
| 1# target frequency decrease value (Boost mode) |  | 00F6 |  |  | Hz
| 2# target frequency decrease value (Boost mode) |  | 00F7 |  |  | Hz
| 1# water temperature for decreasing target frequency (ECO mode) |  | 00F8 |  |  | ℃
| 2# water temperature for decreasing target frequency (ECO mode) |  | 00F9 |  |  | ℃
| 1# target frequency decrease value (ECO mode) |  | 00FA |  |  | Hz
| 2# target frequency decrease value (ECO mode) |  | 00FB |  |  | Hz
| 1# water temperature for decreasing target frequency(Cooling mode) |  | 00FC |  |  | ℃
| 2# water temperature for decreasing target frequency(Cooling mode) |  | 00FD |  |  | ℃
| 1# target frequency decrease value(Cooling mode) |  | 00FE |  |  | Hz
| 2# target frequency decrease value(Cooling mode) |  | 00FF |  |  | Hz
| Ambient temperature for allowing to decrease target frequency (Heating mode) |  | 0100 |  |  | ℃
| Ambient temperature for allowing to decrease target frequency (Cooling mode) |  | 0101 |  |  | ℃
| Exhaust temperature to maintain EEV opening |  | 0102 |  |  | ℃
| Reserve |  | 0103 |  |  | Hz
| Reserve |  | 0104 |  |  | Hz
| Reserve |  | 0105 |  |  | Hz
| Reserve |  | 0106 |  |  | Hz
| Reserve |  | 0107 |  |  | Hz
| Reserve |  | 0108 |  |  | Hz
| Reserve |  | 0109 |  |  | Hz
| Reserve |  | 010A |  |  | Hz
| Max allowable operating ambient temperature |  | 010B |  |  | Hz
| Min allowable operating ambient temperature |  | 010C |  |  | Hz
| Upper limit value of compressor frequency （Cooling mode） |  | 010D |  |  | Hz
| Lower limit of compressor frequency（Cooling mode） |  | 010E |  |  | Hz
| Reserve |  | 010F |  |  | Hz
| Reserve |  | 0110 |  |  | Hz
| Reserve |  | 0111 |  |  | Hz
| Reserve |  | 0112 |  |  | Hz
| Reserve |  | 0113 |  |  | Hz
| Reserve |  | 0114 |  |  | Hz
| Reserve |  | 0115 |  |  | ℃
| Reserve |  | 0116 |  |  | ℃
| Reserve |  | 0117 |  |  | ℃
| EEV opening for oil return operation |  | 0118 |  |  | P
| Reserve |  | 0119 |  |  | /
| Reserve |  | 011A |  |  | /
| Reserve |  | 011B |  |  | /
| Reserve |  | 011C |  |  | /
| Reserve |  | 011D |  |  | /
| Reserve |  | 011E |  |  | /
| Reserve |  | 011F |  |  | 、
| Reserve |  | 0120 |  |  | /
| Reserve |  | 0121 |  |  | /
| Reserve |  | 0122 |  |  | /
| Reserve |  | 0123 |  |  | /
| Reserve |  | 0124 |  |  | 、
| Reserve |  | 0125 |  |  | /
| Reserve |  | 0126 |  |  | /

## code
address | bit | code
C13 (0x000C) Sensor failure | bit0 | E21 | Ambient temperature failure
| bit1 | NA
| bit2 | E27 | Water outlet sensor failure
| bit3 | E15 | Water inlet sensor failure
| bit4 | NA
| bit5 | E18 | Exhaust sensor failure
| bit6 | E16 | Outside coil sensor failure
| bit7 | E29 | Return air temperature sensor failure
| bit8 | NA
| bit9 | E07
| bit10 | E08
| bit11 | E11 | After throttle temperature sensor failure
| bit12 | NA
| bit13 | NA
| bit14 | NA
| bit15 | NA
C14 (0x000D) System failure | bit0 | E12 | Exhaust temperature too high
| bit1 | E05 | High pressure protection
| bit2 | E06 | Low pressure protection
| bit3 | E03 | Water flow failure
| bit4 | E32 | Water outlet temperature over in Heat Mode
| bit5 | E23 | Outside coil temperature over in Cooling Mode
| bit6 | E22 | Vast temperature variations between inlet and outlet
| bit7 | E24 | Stop running in emergency(mother board)
| bit8 | E25 | EEprom of mother board is in error
| bit9 | E46
| bit10 | E33 | Outside coil temperature over in Cooling Mode
| bit11 | E10 | connection failure between driver and mainboard
| bit12 | E04
| bit13 | E30 | Protection during the outdoor ambient temperature is too low
| bit14 | NA
| bit15 | E09 | connection failure between control mainboard and controller
C15 (0x000E) Driver failure | bit0 | NA
| bit1 | E34 | Compressor drive failure
| bit2 | E35 | Compressor current over
| bit3 | E36 | Compressor phase output failure
| bit4 | E37 | IPM current failure
| bit5 | E38 | Drive module temperature is too high
| bit6 | E39 | Stop running in emergency(drive board)
| bit7 | E40 | DC voltage is too high
| bit8 | E41 | DC voltage is too low
| bit9 | E43 | AC voltage is too low
| bit10 | E44 | AC current is too high
| bit11 | E45 | EEprom of drive board is in error
| bit12 | NA
| bit13 | NA
| bit14 | NA
| bit15 | NA
C16 (0x000F) Output status | bit0 | compressor | 0: OFF / 1: ON
| bit1 | 4-way valve | 0: OFF / 1: ON
| bit2 | AUX | 0: OFF / 1: ON
| bit3 | NA
| bit4 | NA
| bit5 | NA
| bit6 | Water pump | 0: OFF / 1: ON
| bit7 | Chassis heating belt | 0: OFF / 1: ON
| bit8 | Crankshaft heating belt | 0: OFF / 1: ON
| bit9 | NA
| bit10 | NA
| bit11 | NA
| bit12 | NA
| bit13 | NA
| bit14 | NA
| bit15 | NA
C17 (0x0010) Working status | bit0 |  | 1:defrost operation
| bit1 | NA
| bit2 | NA
| bit3 | NA
| bit4 | NA
| bit5 | NA
| bit6 | NA
| bit7 | NA
| bit8 | NA
| bit9 | NA
| bit10 | NA
| bit11 | NA
| bit12 | NA
| bit13 | NA
| bit14 | NA
| bit15 | NA